## Equipment_Schedule
Source Part | Clause/Section | PDF Page | Equipment/Item | Quantity | Rating/Specification | Standard Reference | Notes
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 50 | OHL Feeder Modules | 4 | The feeder module consists of bus bars, but not limited to the following main devices: R a. One (1) no. 1600A, three-phase circuit breaker. b. Two (2) nos. 1600 A, motorized three-phase bus bar disconnector switches along with maintenance earthing switch, One (1) no. 1600 A motorized three-phase line disconnector switches along with N maintenance earthing switch, 1 (One) No. three- phase high speed type earthing switch with motor spring charged type. Bus bar disconnect switch shall be with bus transfer current capability. c. One (1) no. three-phase voltage transformer or three (3) nos. single-phase voltage transformers, with isolating device (disconnect link or separate disconnect switch). The VT requirements shall be as per Appendix-IX and SLD. d. The metering CTs shall have (2) independent & identical Current Transformer metering cores with accuracy class of 0.2FS5. e. For protection Current Transformers specification shall be as per Appendix-IX. f. The Current Transformers shall be as per Appendix- g. The metering CTs shall be equipped with 2 Nos. CT core for main and check revenue metering as per Saudi Arabian grid code. h. For Line Feeders Termination: One (1) no. 1600A, indoor/outdoor, GIS bus duct sections for connection up to and including SF6-air bushings for outgoing feeder to HV OHTL connection complete with all accessories. Cable Feeder Modules | isolating
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 50 | Cable Feeder Modules | 2+1 | (inter The feeder module consists of bus bars, but not limited tie) to the following main devices: + (spa re) TO BE USED FOR a. One (1) no. 1600A, three-phase circuit breaker. MATERIALS UNTIL b. Two (2) nos. 1600 A, motorized three-phase bus bar disconnector switches along with maintenance WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ A Item # Unit QTY D E S C R I P T I O N ’ earthing switch, One (1) no. 1600 A motorized three-phase line disconnector switches along with maintenance earthing switch, 1 (One) No. three- phase high speed type earthing switch with motor spring charged type. Bus bar disconnect switch R shall be with bus transfer current capability. c. One (1) no. three-phase voltage transformer or three (3) nos. single-phase voltage transformers, with isolating device (disconnect link or separate disconnect switch). The VT requirements shall be N as per Appendix-IX and SLD. d. The metering CTs shall have (2) independent & identical Current Transformer metering cores with accuracy class of 0.2FS5. e. For protection Current Transformers specification shall be as per Appendix-IX. f. The Current Transformers shall be as per Appendix- g. The metering CTs shall be equipped with 2 Nos. CT core for main and check revenue metering as per Saudi Arabian grid code. h. One (1) no. 1600A, indoor/outdoor, GIS bus duct indoor/outdoor, Gas insulated cable connection chamber suitable to accommodate 145kV class, 1C outgoing feeder connection complete with all accessories. Transformer Feeder Modules with GIB | isolating
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 51 | Transformer Feeder Modules with GIB | 2 | The feeder module consists of bus bars, but not limited to the following main devices: b. Two (2) nos. 1600 A, motorized three-phase bus bar disconnector switches along with maintenance earthing switch. Bus bar disconnect switch shall be with bus transfer current capability. c. One number Maintenance earthing switch after circuit Breaker. TO BE USED FOR MATERIALS UNTIL d. One (1) no. three-phase voltage transformer or three (3) nos. single-phase voltage transformers, with isolating device (disconnect link or separate WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ A Item # Unit QTY D E S C R I P T I O N ’ disconnect switch). The VT requirements shall be as per Appendix-IX and SLD. e. The Current Transformers shall be as per Appendix- E f. One (1) no. 1600A, indoor/outdoor, GIS bus duct sections for connections up to and including SF6-air bushings for outgoing feeder to power transformer connection complete with all accessories. Bus Coupler Module: | isolating
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 52 | Bus Coupler Module | 2 | bus bars, but not limited to the following main devices: a. One (1) no, 2000A, three-phase circuit breaker. b. Two (2) nos. 2000A, motorized three-phase disconnecting and grounding switches. Bus bar disconnect switch shall be with bus transfer current capability. c. Two CT’s on both side of circuit breaker and each CT shall have number of cores as per Appendix-IX. Bus Section Module with Circuit Breaker:
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 52 | Bus section module | 1 | bus bars, but not limited to the following main devices: a. One (1) no. 2000A, three phase circuit breaker. b. Two (2) nos. 2000A, motorized three-phase disconnecting and grounding switches. Bus bar disconnect switch shall be with bus transfer current capability. c. Two (2) CT’s for upper (front) bus and each CT shall have number of cores as per Appendix-IX. Bus Section Module without Circuit Breaker:
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 52 | Bus section module | 1 | bus bar, but not limited to the following main devices: TO BE USED FOR MATERIALS UNTIL disconnecting and grounding switch. Bus bar disconnect switch shall be with bus transfer current capability. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ b. Two (2) CT’s for lower (rear) bus and each CT shall ’ have number of cores as per Appendix-IX. Bus VT Module:
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 53 | Bus VT module | 4 | but not limited to the N following main devices: a. One (1) No. motorized grounding switch. b. One (1) No. three-phase voltage transformer or three (3) Nos. single-phase voltage transformers, with isolating device (disconnect link or separate disconnect switch).The VT requirements shall be as per Appendix-IX and SLD. | isolating
APPENDIX XXVI - SAFETY AND SECURITY REQUIREMENTS | 12.2.1.2 | 53 | Bay Control Panels (BCPs) | 1 | which shall consist of Bay Control Units (BCUs)/Bay Protection Units (BPUs)/ Bay Emergency Control Units (BECUs), instead of conventional Local Control Panels (LCPs). BCU shall house control IEDs having local HMI and also provide the functions of shall operate at bay level only under emergency due to failure of BCUs or any other SAS related components, independent from BCUs via conventional mimic. The BPU shall be designed to accommodate the bay units of the bus bar differential protection of a particular bay, integral with breaker failure protection. The BCPs shall be designed to accommodate both copper & fiber optic cables with necessary loop length. The BCU/BPU shall be designed to meet all the requirements as per Appendix-IX and Appendix-XIII, Appendix XVII and TES-P-107.01
Appendix XVII | 12.2.1.2 | 53 | SF6 gas density and leakage monitoring equipment | 1 | SF6 gas density and leakage monitoring equipment.
Appendix XVII | 12.2.1.2 | 53 | Structural supports | 1 | GIS designed and fabricated to withstand the short circuit forces. Notes 1. The 110 kV GIS Switchgear shall be equipped with Internal Partial discharge measurement Sensors as per 32-TMSS- 02, 38-TMSS-07. PD monitoring system is not required. GIS equipment arrangement for double bus single breaker configuration in GIS building/room shall follow the following criteria: 1) Bus Bar No.1 = Lower Bus Bar = Rear Bus Bar TO BE USED FOR MATERIALS UNTIL 2) Bus Bar No.2 = Upper Bus Bar = Front Bus Bar and connected with Bus Bar isolator (06). WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 3) Bus section circuit breaker is located with Bus Bar No.2. ’ 4) Substation equipment arrangement shall be as per Substation Layout drawings. 2. 110/13.8 kV Power Transformer Design, manufacture, Factory test, supply, install, Test and commission of power transformers complying with the requirements stipulated in 53-TMSS-01 and 01- TMSS-01 with the following basic design data: | isolator
Appendix XVII | 12.2.1.2 | 54 | Power transformers | 2 | 50/67MVA, ONAN/ONAF, YNyn0+d1, 3phase, 60Hz, with 22% impedance @ 50MVA base, oil immersed power transformers complete, OLTC range +12.5% to -20% with step voltage 1.25%, HV (Oil/Air bushings, 40kA/1sec), MV condenser bus termination enclosure & all other accessories and appurtenances as per 53-TMSS-01 complete with bushing CTs, and suitable brackets for mounting surge arrestor. The total guaranteed ONAN losses of the power transformer shall not exceed 209 kW.
Appendix XVII | 12.2.1.2 | 54 | 96 kV outdoor surge arresters | 6 | station class SM as per table 1 of IEC-60099-4 and 35-TMSS-01, metal-oxide surge arresters along with surge counters, complete, mounted on suitable brackets on power transformer | IEC-60099-4
Appendix XVII | 12.2.1.2 | 54 | Power transformer secondary Neutral | 2 | Each power transformer secondary Neutral shall be grounded via NGR confirming to 57-TMSS-01. The neutral grounding resistors (NGRs) rated (5.3 ohms, 1500 Amps for 10 sec. Earthing Resistor with built-in-DS, CTs as per Appendix-IX, Structural material, terminals, alarm indicators, labeling etc. as per specifications) to the power transformers MV Neutral Bushings. Notes: a. The Power Transformers HV (Phase/Neutral) shall be Neutral of power transformer shall be solidly grounded, Bidder shall use copper strip mounted on suitable insulators to bring HV Neutral connection up to bottom of power transformer and connect this strip to grounding mesh as per TES-P-119-10. b. Power Transformers shall be designed with wheel moving facilities which can be detached at the site as TO BE USED FOR per 53-TMSS-01 and used as SKID type base Power MATERIALS UNTIL Transformers. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ A Item # Unit QTY D E S C R I P T I O N ’ c. Optical Fiber Sensors for direct measurement of Winding Hot Spot Temperature with their related complete monitoring system shall be installed in the outdoor Power Transformer local control cabinet. d. Three (3) nos. sensors shall be installed on each central phase and one (1) nos. on each lateral phase of HV & MV windings. e. The Power Transformer local control cabinet shall be equipped with 400/110V step down transformer with ac 3 2 1 a center tap grounded secondary as per TES-P- 119.26. f. DGA is not required, contractor shall ignore requirement of 53-TMSS-03. 3. MV SWITCHGEAR MV indoor metal-enclosed or Gas Insulated switchgear with SF6 or vacuum breakers, 25kA/3sec. short circuit capability, as per 32-TMSS-01 Or 32-TMSS-03, Single Line Diagram, Appendix-XVII and Substation Layout drawings and consisting of the following main equipment: 13.8kV, 3600A, 60Hz at 400 C MV switchgear, comprising:
Appendix XVII | 12.2.1.2 | 55 | Bus section Panels | 1 | 3600A.
Appendix XVII | 12.2.1.2 | 55 | Transformer Panels | 2 | 3600A with additional C.T core for Check Metering
Appendix XVII | 12.2.1.2 | 55 | Service transformer Feeder Panels | 2 | 630A with additional C.T core for Check Metering
Appendix XVII | 12.2.1.2 | 55 | Feeder Panels | 2 | 1250 for STATCOM.
Appendix XVII | 12.2.1.2 | 55 | Feeder Panels | 4 | 630A.
Appendix XVII | 12.2.1.2 | 55 | Space for future feeders | 12 | Space for future feeders
Appendix XVII | 12.2.1.2 | 55 | Metering Feeder Panel with one (1) three (3) phase or three (3) | 1/bus | Metering Feeder Panel with one (1) three (3) phase or three (3) Each single phase VTs for each bus as per SLD. Note: metering panel and bus riser transition panel can be accommodated in one panel.
Appendix XVII | 12.2.1.2 | 55 | Three-phase bus ducts or insulated bus bars and adapters | 1 | for interconnection of Bus-2 & Bus-3. (if required) TO BE USED FOR MATERIALS UNTIL WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ A Item # Unit QTY D E S C R I P T I O N ’
Appendix XVII | 12.2.1.2 | 56 | Incomer | 1 | Auxiliary transformer and all outgoing feeders shall be equipped with two (02) independent & identical metering Current Transformer cores with accuracy class 0.2FS5. - Other metering CTs as per approved OPDS. For protection, Current Transformers specification shall be as per Appendix-IX. |  | approved
Appendix XVII | 12.2.1.2 | 56 | Accessories & devices as required with the following | 1 | Accessories & devices as required with the following:- 1. Three phase bus bars and grounding switches. 2. Control & protection IEDs. 3. Synchro check functions for incomers and bus coupler. 4. Auto-reclosing functions for outgoing feeders. Note  Other switchgear accessories as per Single Line Diagram and Substation Layout drawings  All devices, accessories, wiring for integrating with SAS and along with hard wired control with indications available to facilitate operation during emergency (in case of failure of Control IED or any other SAS related components).  The incomers shall be suitable for termination of Solid insulated condenser bus bar to take feed from Power transformer,  The clearances indicated in Substation Layout drawings for MV switchgear room are the minimum requirements to be followed. However, the same shall be adjusted based on manufacturer recommendation and submit the same for COMPANY review and approval during base design stage. The front and rare clearance of the switchgear shall be in  The MV switchgear supplied for Capacitor Banks shall be suitable for automatic switching of 3x7MVar. Incomers, Bus ties and outgoing feeders for capacitor banks shall be suitable for capacitive current switching. Moreover, back- to-back switching capability for capacitor banks and bus tie circuit breakers shall be in accordance with IEC-62271-100 which shall be proven by type test reports. TO BE USED FOR MATERIALS UNTIL WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 4. +/- 20 MVAr, STATCOM ’ | IEC-62271-100
Appendix XVII | 12.2.1.2 | 57 | Contractor to Design | 2 | manufacturer, supply, install, test and commission +20MVAr (Capacitive) and -20 MVAr (Inductive) STATCOM with 20% overload capability, P complete with all required equipment, apparatus, Power cables, LV AC/DC, power, control and instrumentation (shielded) and communication interface cables, grounding, shielding system, control system, protection system, SAS system. Fire detection, alarm and annunciation and protection system. Alarm and. annunciation system. All required civil works, electromechanical works etc. Contractor shall follow PART-II of PTS-21WN1008 for detailed scope of work for STATCOM. 5. Power Cables,OHL HV Terminations & MV connection MV cables connecting Power Transformers, STATCOM, Station Service Transformers, and/to MV Switchgear. LV cables connecting Station Service Transformers and/to AC main distribution board: i. One (1) lot: MV, single core, copper XLPE cable to connect the proposed STATCOMs to MV Switchgear; along with cable terminations. The size of the cable shall be 1C×630mm2 and the number of cables/phase shall be based on calculation, minimum two (2). Station Service Transformers to MV Switchgear, along with cable terminations. The size of the cable shall be 1×3C×300mm2. iii. One (1) Lot: MV, Single Core XLPE copper cable to connect the proposed Neutral Grounding Resistors with transformer neutral. The size of the cable shall be 1Cx 630 mm2. iv. One (1) lot: MV terminal lug/pad for Copper or Aluminum conductor size CC1 figure C2 with 12mm (1/2 in) bolt and conductor size of (400mm2 or above) shall be with 4-hole as per NEMA CC1 figure C3 with 12mm (1/2 in) bolt. v. One (1) lot: LV, four cores, copper XLPE cable to connect the proposed TO BE USED FOR Station Service Transformers to AC main distribution board, along with cable terminations lugs. The size of the cable MATERIALS UNTIL shall be 2 Run of 4×1C×400mm2 (Minimum), actual size and runs of cable shall be as per calculations. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ vi. One (1) lot: Cable trays and supports, Tags, ferrules etc. for MV XLPE cables of all MV outgoing feeders from MV switchgear. ’ vii. One (1) lot: Cable trays and supports for HV XLPE cables of all HV outgoing feeders from HV switchgear. N b. HV GIS connecting to Overhead T/L lines: i. One (1) Lot: OHTL contractor will terminate slack span to substation gantry and will provide lose phase conductor only (about 600meters) to substation contractor for connection to the substation equipment. Substation contractor have to arrange connectors for all their substation equipment’s. ii. One (1) Lot: The necessary hardware & accessories including but not limited to (jumper conductors, insulators & its hardware and other accessories) for termination at GIB (SF6 to air bushing) from the gantry structure shall be provided by the Substation Contractor. The installation and connection of the substation terminal equipment at these points shall be made by substation contractor. Ii One (1) Lot: all accessories required to terminate the inter connection with terminal equipment near the Gantry structures. i. Three (3) Nos./Circuit., 96 outdoor, station class SM as per table 1 of IEC- 60099-4, metal-oxide surge arresters as per 35-TMSS-01 along with surge counters, complete with steel support structures near the gantry structure for the incoming & outgoing feeders. The construction of HV take-off structures for termination of OHTLs is part of Substation Scope. However the connection of OHTL to gantry is under OHTL contractor scope c. HV connecting GIS to Power Transformers: iii. One (1) Lot: 1-795 kcmil ““CONDOR”, ACSR/AW overhead conductor per phase with termination hard wares and accessories between HV outdoor SF6/Air bushing and Transformer HV bushing/surge arresters. o d. 13.8 kV Fully Insulated Bus Bars & Associated accessories at 55 C. i. One (1) Lot: Outdoor/Indoor Solid Insulation System (SIS) comprising insulated condenser Bus Bars suitable for 13.8 kV, 3600A, 60Hz 25kA/3 Sec per phase, connecting LV side of, 110/13.8 kV Power Transformers along with cable compartment of 13.8 kV, 3600A, Transformer Incomer Switchgear Panels complete with termination assembly, hardware and accessories. TO BE USED FOR e. Power Cables and Terminations for MV STATCOM MATERIALS UNTIL i. One (1) lot: MV, single core, copper XLPE cable to connect the proposed STATCOMs to MV Switchgear; along with cable terminations. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ The size of the cable shall be 1C×630mm2 and the number of cables/phase shall be based on calculation, minimum two (2). ’ ii. Lot: 13.8kV XLPE/AIR Interface cable-sealing ends (for a rated current of 1250A continuous with 25kA at 3sec. short circuit withstand capability) suitable for termination of 3X1Cx300 mm², Copper, XLPE cable complete N with all accessories to connect the 13.8kV switchgear to the new 13.8kV P STATCOM unit end complete clamps and connectors. iii. Lot: MV Power cables, as necessary to interconnect STATCOM System as per COMPANY standards (for transformer coupling option). iv. Splicing, testing & termination of MV cables between STATCOM system & 13.8kV Switchgear as per COMPANY standards. Note:- A. As per 11-TMSS-04, the metallic shield shall be 35 mm2 for MV cables of more than 70 mm2 conductor area. B. All HV & MV cable installations (as applicable) in Substations’ basements, vaults, tunnels and manholes (as applicable) shall be fire retardant. Fire retardant cable installation can be achieved through either “cable outer sheath is fire retardant rated” or “painted with fire retardant paint”. In case, the HV and MV cables outer sheath is not fire retardant, HV cables shall be painted with 3 hours fire rated “fire retardant paint” throughout the whole length inside the basements, vaults, tunnels and manholes. The same shall comply with applicable clauses of TES-P-104.05 and TES-P-119.21. The “fire retardant paint” shall comply with TES-H-107.01. 6. Bonding & Grounding of Cables The HV& MV cables shall be single point bonded. The CONTRACTOR shall furnish calculations for COMPANY review/approval. 7. RTV Silicone Rubber Insulator Coating The CONTRACTOR shall apply RTV Silicone Rubber Insulator Coating on all outdoor porcelain insulators/bushings, which are supplied and installed under the scope of this project including GIS and POWER TRANSFORMER insulators/bushings to meet the COMPANY requirements as per 15-TMSS-07 & 01-TMSS-01. 8. Station Service transformers Two (2) nos. each: 1000kVA, Dyn11, MV-400/230V, 3-phase, 60 Hz, 5% impedance, ONAN, station service transformers with all appurtenances and accessories as per 51-TMSS-01 and Appendix - XX. The final size shall be based on calculation (STATCOM load shall be considered as (120KVA/per STATCOM)) TO BE USED FOR 9. AC Auxiliary Power Supply MATERIALS UNTIL One (1) lot: 2000A (Minimum), 400V, 3Ø and 230V 1Ø AC power supply system as per Appendix- XX and TES-P-119.30 (Figure 30-1), with auto WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ transfer scheme system, AC main distribution board, sub- distribution panel boards as per 31-TMSS-02 complete with ’ breakers, wires/cables, conduits, trays, etc. Metering functions and alarms of AC auxiliary power system shall be integrated with SAS. 10. DC Auxiliary Power Supply (125V DC) P One (1) lot: DC auxiliary power system as per TES-P-119.30 (Figure 30-3) with panel-mounted Gel type VRLA (OPzV) battery bank as per latest revision of 46-TMSS-04 with a minimum capacity of 2500 Ah on 10 hour basis (minimum). No. of panels for Gel type battery banks shall be provided as required. Two (2) nos. 400A (minimum) rated battery chargers compatible with battery and as per 46-TMSS-02, main DC distribution board, sub-distribution panel boards as per 31-TMSS-02 complete with breakers, wires/cables, conduits, trays, etc. Metering functions and alarms of DC auxiliary power system shall be integrated with SAS. Battery High Impedance Alarm Monitoring Relay as per TES-P- 119.30. Gel Battery shall be as per the following international standard: - IEC 60896-21: Stationary lead-acid batteries Part 21: Valve regulated types – Methods of test. - IEC 60896-22: Stationary lead-acid batteries Part 22: Valve regulated types Requirements. Gel Battery installation shall be as per the following safety international standard: - IEC 62485-2: Safety requirements for secondary batteries and battery installations - Part 2: Stationary batteries. Gel Batteries & charger panels are to be installed in the control room. Therefore, provided battery solution as well as charger shall be designed in a way that allows safe installation with no special explosion-proof or ventilation requirements, e.g. provided charger shall be capable of providing the required current and floating and recharge voltage required by the batteries, without causing any hazard in the control room. 11. Low Voltage Power, Control, Instrumentation (Shielded) and Communication Interface Cables One (1) lot: Multi-core and/or multi-pair control cables and low voltage AC/DC and shielded instrumentation and communication interface cables as per 11-TMSS-10 & TES-P-119.29, as necessary to interconnect various substation equipment and devices to achieve a complete working system for this PROJECT, complete with conduits and TO BE USED FOR trays. MATERIALS UNTIL Note: grounding wire shall be separate and not part of power cables. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 12. Lighting System and Small Power Requirements ’ One (1) lot: Indoor and outdoor lighting including emergency lighting system shall be LED Type. LED type lamps, fixtures, supports, switches, light control devices, conduits, trays, and wiring required to complete the installation shall be as per TES-P-119.25 with the N addition of the relevant international standards. P Sensors/light controls shall be used for control of indoor and outdoor lighting. Indoor lighting control shall be designed such that light is on only when there is a personnel present in the room/building. Outdoor lighting, on the other hand, shall be controlled by light sensor/photo-cell. All control schemes shall allow for manual operation of the lighting system. Light control and control scheme shall be accepted and approved by COMPANY. One (1) lot: Indoor and outdoor (weatherproof) receptacle outlets, conduits, trays, and wiring required to complete the installation as per TES-P- 119.25. TO BE USED FOR MATERIALS UNTIL WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 13. Grounding System ’ One (1) lot: Grounding system complete with grounding conductors, ground rods and associated accessories to meet the COMPANY requirements as per TES-P-119.10. N The grounding grid shall be provided in the asphalted Substation P area (Substation area as per layout drawing) within the substation boundary wall and extend at least 1.5 meters on all sides. The soil resistivity values (electrical and thermal) to be used for substation grounding system design and ampacity calculations shall be based on the values to be performed by CONTRACTOR as per Appendix-XI. 14. Shielding System One (1) lot: Shielding system complete with shield wires, lightning masts and associated accessories to meet the COMPANY requirements as per TES-P-119.07. The Shielding system shall be designed to cover the whole Substation area (Substation area as per layout drawing). B. Source Substation (Remote Ends) B.1 “MODAN BSP” Source Substation (Remote End # 1): 1. Low Voltage Power, Control, Instrumentation (Shielded) and Communication Interface Cables One (1) lot: Multi-core and/or multi-pair control cables and low voltage and shielded instrumentation and communication interface cables, as necessary to interconnect various substation equipment and devices to achieve a complete working system for this PROJECT. Note:  AC/DC auxiliary power supply system for new line protection panels under the scope of this PTS shall be fed from existing AC/DC Main Distribution boards of Source Substation. In case the feeders are not adequate, Contractor shall a. One (1) AC Sub distribution board per section 6.02. b. One (1) DC Sub distribution board per section 6.02. Contractor shall supply, lay, and terminate (at both ends) the required low voltage cables for the same. TO BE USED FOR  Grounding wire shall be separate and not part of power cables. MATERIALS UNTIL One (1) lot: Provide grounding connection between the proposed equipment and the main ground mat (being provided by others under separate PROJECT). WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 2 The HV GIS switchgear bays (i.e. Circuit breakers <<AXXX˃˃ & <<AXXX˃˃) shall ’ be used to feed New Substation. Data to be collected at Site visit. B.2 “SHB-1 P. Plant “Source Substation (Remote End# 2): N 1. Low Voltage Power, Control, Instrumentation (Shielded) and Communication P Interface Cables One (1) lot: Multi-core and/or multi-pair control cables and low voltage and shielded instrumentation and communication interface cables, as necessary to interconnect various substation equipment and devices to achieve a complete working system for this PROJECT. Note:  AC/DC auxiliary power supply system for new line protection panels under the scope of this PTS shall be fed from existing AC/DC Main Distribution boards of Source Substation. In case the feeders are not adequate, Contractor shall supply the following. a. One (1) AC Sub distribution board per section 6.02. Contractor shall supply, lay, and terminate (at both ends) the required low voltage cables for the same.  Grounding wire shall be separate and not part of power cables. One (1) lot: Provide grounding connection between the proposed equipment and the main ground mat (being provided by others under separate PROJECT). used to feed New Substation. Data to be collected at Site visit. 4.03 SAS/CONTROL, INDICATION, INTERLOCK SYSTEM & PROTECTIVE RELAYING SYSTEM A. Substation Automation System (SAS) The Substation Automation System (SAS) for New Substation shall conform to the requirements stipulated in Appendix-XIII & TES-P-107.01. B. Control and indication System 1. General TO BE USED FOR Operator & Engg. Work stations, Protection Panels, Interface panels, Server Panel, Gateway Panel, Communication Panel, AMI Panels, ACCS, ACSE / MATERIALS UNTIL TOP Etc. The Operator & Engg. Work Stations, shown in the drawing are indicative only, which shall meet the PROJECT requirements in all respects, WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ the details of which will be decided during the base/detail design stage of the PROJECT. ’ b. The SAS shall be designed conforming to the requirements stipulated in Appendix-XIII. The control and indication system shall be integrated with SAS. The control system functional requirements shall also conform to N COMPANY standard TES-P-119.26. The following control levels shall be provided for the HV & MV circuit breakers control: i. Local Control from the Panels in the HV GIS room / MV Switchgear room through local HMI or from the hardwired mimic control (in case of failure of control IED or any other SAS related components) of the Bay Control Panel (BCP) / Switchgear. The remote position of Local/Off/Emergency/Remote (4-position switch) selection shall transfer breaker controls to the Station HMI and to the Power Control Center (PCC) through Station Communications Gateway, Communication system and SCADA depending upon the position of local/supervisory (soft) selection on Station HMI. ii. Remote Control from the Station HMI and Power Control Center for the control of CBs. The Supervisory position of Local/Supervisory (soft) selection enables control from PCC. iii Supervisory Control from Power Control Center (PCC) via SCADA, Communication System and gateway. c. Bay Control Panels (BCPs) shall be completely wired and adequate terminal blocks shall be provided for the termination of external incoming cables. 2. New Substation a. The Contractor shall provide a complete modern Substation Automation System (cutting edge technology) for the below given controls, conforming to the detailed specifications provided in Appendix-XIII. The panels for the same shall conform to 31-TMSS-01. (i) Local Control at Bay levels and Station Control facilities with all required items. Refer to Section 6.03 for further details. (ii) Supervisory Control from SCADA i.e. Power Control Center (PCC) b. The Contractor shall provide an integrated control system along with MV Switchgear in accordance with COMPANY material standards 32-TMSS-01 (with the exception that the conventional meters, relays and transducers shall be replaced by control and Protection IEDs) and applicable requirements of 31-TMSS-01 c. HV and MV Control System: TO BE USED FOR MATERIALS UNTIL The control system for HV GIS and MV metal-enclosed indoor switchgears shall be provided conforming to the requirements stipulated in section 6.03 of WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ this PTS. The Control IEDs shall be provided to carry out the above control functions and shall be integrated with SAS. ’ d. Automatic Capacitor Control System (ACCS) Requirements: (N.A) P e. ACSE/TOP Requirements: (N.A) f. Automatic Voltage Control (AVC) Requirements: One (1) AVC panel for each HV/MV transformer shall be provided. The AVC panel shall be as per 31-TMSS-01 and TES-P-119.26. The 400/110Vac control transformer referred in TES-P-119.26 for the AVC should be located in the respective OLTC/Transformer outdoor local control cabinet. For details, refer to Appendix XXIV. B-1 Source Substation Remote End # 1(MODN) Substation Existing substation is SAS (IEC 61850) based substation The CONTRACTOR shall made & modify all the necessary changes in (SAS HMI, i.e. mimic, change in line designation, labeling, etc. for the proposed New Substation–Source Substation HV lines). B-2 Source Substation Remote End # 2 (SHB-1) Substation Existing substation is Conventional SCADA based substation, The contractor shall modify all the necessary changes in (i.e. mimic control, annunciator, alarm check back status indication, change in line designation, labeling, etc. for the proposed New Substation–Source Substation HV lines. C. Electrical Equipment Interlocking 1. General The CONTRACTOR shall provide and install all applicable electrical equipment interlocking requirements for safe operation of the electrical system related to the equipment being provided under this project. The CONTRACTOR shall provide a detailed interlocking scheme to the COMPANY for approval. Necessary auxiliary relays, interlock solenoids, contacts, etc. required (for hardwired interlocks) to facilitate the implementation of interlocking system shall be provided. 2. MV Switchgear Refer to section 6.03 of this PTS for details. D. Protective Relaying TO BE USED FOR For Protective System Relaying, Transient Fault Recorder and SOE requirements refer MATERIALS UNTIL to Appendix-IX. Required IEDs shall be provided for various protective relay functions, which shall be integrated with SAS. The IEDs of HV protection system shall be housed in Bay Control Panels/ Bay Protection Panels. The IEDs of MV protection system shall WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ be housed in MV compartment of MV Switchgear. The CONTRACTOR shall provide protection and control IEDs separately if space is available in MV Switchgear panels. ’ If space is not adequate, the same may be combined. 4.04 SAS/METERING SYSTEM A. New Substation E 1. The minimum metering devices/scales to be provided on the panels, other than SAS equipment, shall be as per Amendment Notification No. 18-00169-30504101 dated May 30, 2018 (as applicable) attached in Appendix XVII. 2. The metering requirements shall be integrated with SAS. with +20% (minimum). Revenue and power quality multifunction meters to be provided and installed in the substation per the Relaying and Metering One Line Diagram, mainly for revenue metering and power quality monitoring, shall conform to COMPANY Standard 40- TMSS-03 & Industrial Ethernet Switch as per 47-TMSS-02 and according to detailed AMI specification in Appendix-II with the following: a. Two (2) Power quality meters complete with its accessories. One (1) Power Quality Meter shall be connected to HV & other one (1) to MV, the VT connection shall be from BUS VTs through bi-stable relay. b. Four (2+2) main and check Revenue meters, complete with its accessories as per Saudi Arabian Grid Code’s (SAGC) and 40-TMSS-03, two (2) for each Power transformer. c. Four (2+2) main and check Revenue meters, complete with its accessories as per Saudi Arabian Grid Code’s (SAGC) and 40-TMSS-03 on 110kV intertie d. Four (2+2) main and check Revenue meters, complete with its accessories as per Saudi Arabian Grid Code’s (SAGC) and 40-TMSS-03, two (1+1) for each Auxiliary transformer, e. Main and Check Meters shall be from different manufacturers duly approved by the COMPANY as per List of Technically Acceptable Manufacturers & (LOTAM). f. The AMI system shall be standalone system independent of SAS. g. Main and Check meters shall operate from separate CT and VT windings h. Panels for main and check Revenue meters with complete accessories conforming to the COMPANY Standard 40-TMSS-03 shall be placed in Control TO BE USED FOR room. MATERIALS UNTIL WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ The CONTRACTOR is responsible to establish the communication link between the AMI system and substation LAN/WAN System with provision the required LAN ’ switches in AMI side. Also, Contractor shall perform all simulation tests to prove the data transfer capability between main and check Revenue Meters (RMs), Power Quality Meter (PQM) and the Master Data Management (AMS-MDM) center in Riyadh. P 5. Revenue Metering for MV Outgoing Feeders Revenue Metering as per 40-TMSS-03 (excluding Power Quality Meters) shall be provided and installed for all MV outgoing feeders (excluding incomers) and station service transformer feeders). Panels for Revenue Metering System shall be placed in the Control Room. Revenue Meter’s Manufacturer/CONTRACTOR shall apply the “Default Configurations” for all MV revenue meters (attached with Data Schedule). Also, Hand Held Unit (HHU) shall be supplied as per standard no. 40-TMSS-03 and shall be configured for connecting and downloading the billing data from these Revenue Meters. 4.05 SAS/ALARM/ANNUNCIATION SYSTEM A. New Substation Provide all alarm /annunciation associated with the equipment being provided, which are generated by IEDs, as an integral part of SAS. Provide Annunciator panel (s) for all other alarms, which are not generated by IEDs and the same shall also be integrated with SAS through numerical interface devices mounted in a separate interface panel. For the list of alarms, refer to section 6.05. B.1 Source Substation Remote End # 1 Modon) Integrate the alarm associated with the HV lines protection to the existing SAS. B.2 Source Substation Remote End # 2 (SHB-Power Plant) Update/expand the existing alarm/annunciation system for providing new alarms. If the existing alarm/annunciation system is inadequate, provide new annunciator panel without marshaling kiosk. 4.06 SAS/SUPERVISORY CONTROL AND DATA ACQUISITION (SCADA) AND SOE SYSTEMS A. New Substation SHB-3 SAS shall be provided with all required SCADA/SOE functions. SCADA and SOE systems shall be integrated with SAS. For integrated SCADA requirements refer to Appendix-VIII and Appendix-XIII. For integrated SOE requirements refer to Appendix-XIII. B.1 Source Substation Remote End # 1 Modon) TO BE USED FOR MATERIALS UNTIL Integrate all required SCADA/SOE system requirements associated with the HV lines to New Substation to the existing SAS as per Appendix- XIII. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ B.2 Source Substation Remote End # 2 (SHB-Power Plant) ’ For SCADA and SOE system requirements, refer to Appendix - VIII. 4.07 COMMUNICATION SYSTEM For communication system requirements, refer to Appendix – VI 4.08 FIRE DETECTION/ALARM AND SAFETY & FIRE SUPPRESSION SYSTEM A. General The WORK shall include supply of equipment, materials, labor and tools for the installation of a complete fire detection/alarm and fire suppression systems for the 3 2 1 below specified building rooms. The WORK shall also include required testing and commissioning for the systems and to execute other related services for the safe, efficient and reliable performance and complete WORK of this PROJECT to the satisfaction of the COMPANY in conformance with the requirements as prescribed below. B. New Substation The WORK shall include, but not limited to, provision and installation of the following: 1. Fire detection/alarm and fire extinguisher equipment shall be provided in:  110 kV GIS Room  Control Room  Clean Agent Cylinder(s) Room  Stairways (Only Fire detection system)  13.8 kV Switchgear Room  Record Room/Office  Workshop  Toilet (Only Fire detection system)  Power Transformers  Auxiliary Transformers  PACU Area  Cable Basement  Customer Rom  Other Substation areas as per TES-P-119.21 2. Clean Agent Fire suppression System shall be provided in:-  13.8 kV Switchgear Room  Control Room TO BE USED FOR  Communication Room  Customer Room MATERIALS UNTIL  Other Substation areas as per TES-P-119.21 WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ The total Flooding of Clean Agent Extinguishing System shall be UL Listed, designed and installed to comply with TES-P-119.21, TES-B-106.05, TES-B106.06, 90-TMSS- ’ 01, 90-TMSS-03, 90-TMSS-04, TES-P-107.02, NFPA 2001 and the requirements of the local regulation SAF of HCIS. Requirements for Telecom shelter (if any) shall also be complied with 48-TMSS-01. 100% reserve tanks shall be provided, filled with quantity as main and connected to the system. Main/Reserve switch shall be installed and must be fully supervised. E Notes: 1. The Contractor shall submit coordination drawings between fire protection piping, nozzles, lightings, HVAC ductwork, cable trays and other related building systems. provided all HV & MV cable installations (as applicable) in Substations’ basements, vaults, tunnels and manholes (as applicable) shall be fire retardant. Company Standards - and TES-P-119.21. & TES-H-107.01. 3. Fire Extinguishers for Whole Project to be located with “15 Meters” Intervals. Intervals. Clean Agent Cylinders Should be located inside Dedicated Clean Agent Cylinder Rooms. 4. Battery for Main FPSP shall be sized for 72 hours stand by time and 30 min alarm & 48 hours stand by time with 30 min alarm time for Conventional Panels. 4.09 SECURITY ACCESS CONTROL (SAC) SYSTEM REQUIREMENTS Provide the following Security Systems for the Substation: a. Security Access Control System (SAC) as per HCIS Standards No. SEC-05 & COMPANY Specification 48-TMSS-18. b. Closed Circuit Television System CCTV System as per HCIS Standards No. SEC-05 & COMPANY Specification 48-TMSS-18. c. Complete Security System to be interfaced to Security Control Center in WRCC. Notes:  These systems shall be designed and constructed according to HCIS references listed in Appendix-II as applicable.  All clauses of TES-P-119.21 are applicable to this PROJECT except the remarks given under item # 4.13 TO BE USED FOR Assessment System (IDAS). MATERIALS UNTIL  Substation Classification shall be class-3 facility according to the HCIS DIRECTIVES 2017 and criteria described in TES-P-119.21 WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’  Risk analysis done by approved Consulting Firms by High Commission of Industrial ’ Security (HCIS) to provide Design and Scope of work for Security system. 4.10 CYBER SECURITY REQUIREMENTS I CONTRACTOR shall provide the cyber security requirements as specified and detailed in Appendix- XXI, TES-P-107.05 & TES-S-102.01, complete in all respects in the main and remote end substations. 4.11 STATCOM REQUIREMENTS O. CONTRACTOR to follow Part-II of this SOW for complete STATCOM requirements. The main CONTRACTOR shall be prequalified for STATCOM work. In case the main CONTRACTOR is not prequalified for STATCOM, then CONTRACTOR has to provide NG prequalified company to execute the STATCOM work. 4.12 CIVIL AND STRUCTURAL WORK The scope and nature of civil & structural works involved in the Design and Construction of this project shall include to this section of the PTS, Appendix-VII, Appendix-XI, Appendix-XIX & SEC's Transmission Engineering, Construction and Material Standards, Transmission Standard Drawings and to S/S general layout drawing (WT-922170). All associated works necessary for successful completion of the project shall form a part including but not necessarily be limited to the following: 1. The proposed general layout Drawing No. WT-922170 of the substation illustrates the general requirements and the CONTRACTOR must demonstrate that all the equipment supplied is adequately catered for in its design and should encompass all related specifications. The CONTRACTOR should follow the dimensions of each room as per layout drawing for installation of the proposed equipment and incase if the proposed equipment is of bigger size then the room sizes shall be suitably adjusted, which will make the equipment operation/maintenance easier and more accessible/efficient within the land available. 2. Clearance of plot including dump material, existing natural strata, any existing and final grading to TCS-Q-113.02. 3. The Geotechnical investigations shall be carried out by CONTRACTOR to Appendix- XI with following requirements: a. Five (5) boreholes (2-15m, 1-12m & 2-10m). b. Five (5) soil electrical resistivity measurements [Shall be measurable in eight (8) directions covering maximum substation plot area]. TO BE USED FOR c. Four (4) soil thermal resistivity measurements. MATERIALS UNTIL d. Two (2) CBR tests. WT-926968 DESALINATION PROJECT (SWPC/SHOAIBA-3), SH OAIBA NG-1288 0 21WN1008 MA KKAH SAUDI ARABIA 112 ’ 4. CONTRACTOR shall design, fabricate and erect the new steel pre-engineered S/S building as per 71-TMSS-03 & TES-P-119.19 and Appendix-XXV (Steel PEB - Design ’ Criteria, Technical Requirements and Materials Specification). 5. CONTRACTOR shall propose (facade design, aesthetic, color, etc.) 3D architectural drawings for the Steel PEB (Sandwich Panels) in close coordination with the supplier N (three options) to harmoniously blend with the surrounding at the initial design stage. 6. The PEB building foundation and basement shall be designed and constructed as per TES-P-119.19 and TES-P-119.18. Basement shall be provided under 13.8kV Switchgear Room, etc. as per conceptual drawings. 7. The PEB building with separate access shall be designed and constructed as per TES-P-119.19 and TES-P-119.18 for a dedicated room for placing the intertie feeder (customer feeder) equipment (i.e. control & protection & metering Split AC, FFS etc.) 8. In case of high groundwater table elevation, contractor to develop substation with raised basement. All required Civil works and equipment like JIB crane etc. is contractor’s responsibility. Design of Substation shall be subjected to NG approval 9. CONTRACTOR shall design and construction manholes (4.5m x 4.5m & 3m deep) for converting HV UG cables to HV GIB. The manholes shall be sized for bending radius & operation/maintenance clearances. 10. Construction of direct buried PVC conduits to route HV cables from manholes to 1500mm outside the substation boundary fence / wall. Each duct shall contain pull wire rope and both ends shall be capped (or) plugged with duct sealing units. 11. In case of high groundwater table elevation, contractor to develop substation with raised basement. All required Civil works and equipment like JIB crane etc. is contractor’s responsibility. Design of Substation shall be subjected to NG approval. 12. CONTRACTOR shall design/construct reinforced concrete foundation for power transformers as per reference drawings in Appendix-XVI. 13. N.A 14. Clause 7.2.3 of TES-P-119.19 shall govern the FFL of substation bu | IEC 60896-21; IEC 60896-22; IEC 62485-2; BSP; IEC 61850; ASTM A572M; ISO-4310-1981; ISOMETRIC; isolators; IEC 62271-209; IEC 60287; IEC 60871-1; IEEE 48; IEEE Standard; IEEE 1300; IEEE Guide; IEEE 575; ASTM American; ASTM Applicable; IEC 4.0; IEEE-404; IEEE-48; ASTM D150; IEC 62217; IEC 60587; IEC 60947-1; IEC 60715; Isolating; IEC Rated; IEC CT; BSL; IEC Magnetizing; Isolated; IEC 60871; IEC ASTM; IEEE C57.109; IEC 60616; IEC 60296; ISO 3104; ISO 2719; ISO 3016; ISO3675; ISO12185; ASTM D971; IEC 60156; IEC 60247; IEC 61620; IEC 60970; IEC 62021-1; IEC 62021-2; IEC 61125; IEC 60814; ISO14596; IEC 60666; IEC 61619; IEC 61198; IEC 60628; IEC 62535; IEC 62697-1; IEC62271-200; ASTM C1202; ASTM C1543; ISO 12944; IEEE C37.94; IEC-101links; IEC-60870-5-10; IEC-60870-5-101; IEC-104; IEC-60870-5-104; IEC 608070-5-101; IEC 608070-5-104; IEC 608070-5; IEEE 1588; IEC 60834-1; isolation; IEC 60255; IEEE 1613; IEC 61850-3; BSPs; IEC 255; BSS; IEEE PORTS; ASTM 01751; ASTM B-209; BS S; isolate; IEC publication; IEC 60529; ANSI C.37.90; IEC -61850; IEEE Guidelines; BS shall; isolator; BS 1A; BS 2A; BS and; BS fitted; BS requirements; IEEE.C.37; BS 3600; IEC61850; BS circuit; BS Each; IEEE C37-99-1990; IEEE CHECKED; IEC Sources; IEC 61000-4; IEC 158-1; IEC 61869-1; IEC 61869-2; IEC 61869-3; IEC 267; IEC 270; IEC 297; IEC 326; IEC 326-6; IEC 352; IEC Standard; IEC 38; IEC 417; IEC 50; IEC 50-441; IEC 51; IEC 60-1; IEC 60146; IEC 60502-1; IEC 60623; IEC 60688; IEC 68-2; IEC 694; IEC 715; IEC 61870; IEC 61968; IEC 61970; BS 142; BS 162; BS 219; BS 4308; BS 4579; BS 5057; BS 6231; BS 6746; BS 7625; BS 7626; IEEE Sources; IEEE 1052-2018; IEEE C37.91-2008; IEEE 80; IEEE 91; IEEE 1115; IEC for; IEEE C57.13.1; IEC 60034; IEEE-80; BS degree; IEC or; ISO 45001; ISO 14001; IEC 62067; Bs-1; IEC to; IEC the; IEC installation; IEC 61850-10; IEC controlled; IEC 60076-5; IEC ers; IEC standards; ANSI CLASS; IEC in; IEC Website; IEC Type; ISO 9001; IEC GTW; BSI; IEC 62927; ASME-A; ASME A13.1; ANSI -Z87.1; ANSI -Z87.1a; ANSI Z41; IEEE and; ISO scales; ISO 9000; IEC and; IEEE i; IEC 60146-1; IEC DIN; IEC 60747-6; IEC 60076; IEC 61000-4-7; IEC 61071-1; IEC 60664; IEEE 518; IEEE 519; IEEE C57-110; IEC 62747; IEC 60747-1; IEC 60747-2; IEC 60747-9; IEC 61803; IEC 62501; IEEE C57.110; IEEE Standards; ANSI Standards; ASTM D624; ASTM D412; ASTM D2240; ASTM 0648; ASTM-F-2160; ASTM-F-2176; ASTM A123; isotropic; ASTM Longitudinal; ASTM D36; ASTM Water; ASTM Resistance; ASTM PREPARED; ASTM E96; ASTM D5; ASTM OPERATING; ASTM D648; ASTM D4396; ASTM D2564; ASTM F402; ASTM D638; ASTM D1505; ASTM D1525; ASTM D1922; ASTM D1709; IEC 62439-3; Isometrics; Iso-View | approved; Certified; rejected; tested; commissioned; verified; pending

## Summary
Data Type | Total Found | High Confidence (>=0.8) | Medium Confidence (0.5-0.8) | Low Confidence (<0.5) | First Seen Page | Last Seen Page
source_doc | 1828 | 1828 | 0 | 0 | 1 | 3087
rating | 2196 | 2191 | 5 | 0 | 1 | 3091
equipment_id | 1095 | 1095 | 0 | 0 | 2 | 3082
notes | 1821 | 1821 | 0 | 0 | 2 | 3089
equipment_type | 2233 | 2233 | 0 | 0 | 3 | 3091
quantity | 506 | 88 | 418 | 0 | 4 | 3082
section_clause | 97 | 97 | 0 | 0 | 10 | 3085
standard | 55 | 49 | 6 | 0 | 25 | 3044
page_ref | 1205 | 1205 | 0 | 0 | 133 | 2896
TOTALS | 11036