## SLD
SHOAIBA-3 110/13.8 kV SUBSTATION
Section | Component | Parameter | Drawing Value | PTS PDF Page | PTS Reference | Note
Remote End | OHL Feeder | No. | 4 | 50 | 4.02.A.1.1A
|  | Freestand CT | 800/1000/1200/1600 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | Freestand CT Vkp | ≥1400/1750/2100/2800 V | 679 | Appendix IX – 110 kV OHL feeder protection
|  | SA | 96 kV, 20 kA, 10 kJ, Class SM, 3/Feeder | 58 | 4.02.A.5.b; 35-TMSS-01
|  | VT | NA | NA | NA
| Cable Feeder | No. | 2 Main + 1 Spare Equipped | 50 | 4.02.A.1.1B
GIS | Type | Arrangement | Double Busbar Single Breaker | 49 | 4.02.A.1
| System Rating | Rating | 110 kV Nominal, 145 kV Rated, 3Ph, 60 Hz, 2000 A Bus, 40 kA/1 s, 40°C | 49; 243-244 | 4.02.A.1; Appendix II / 32-TMSS-02 data schedule
| Bays | OHL Feeder | 4 | 50 | 4.02.A.1.1A
|  | Cable Feeder | 2 | 50 | 4.02.A.1.1B
|  | Transformer Feeder | 2 | 51 | 4.02.A.1.2
|  | Bus Coupler | 2 | 52 | 4.02.A.1.3
|  | Bus Section | 1 | 52 | 4.02.A.1.4–1.5
|  | Spare Equipped | 1 | 50 | 4.02.A.1.1B
|  | Future | 2 | — | —
|  | Bus VT Module | 4 | 53 | 4.02.A.1.6
| Feeder VT | Ratio | 110/√3 kV : 115/√3 V : 115/√3 V | 679; 688 | Appendix IX – 110 kV feeder VT requirements
|  | Burden | 100 VA + 100 VA, Simultaneous Burden 200 VA | 679; 688 | Appendix IX – 110 kV feeder VT requirements
|  | Class | 0.2/3P | 679; 688 | Appendix IX – 110 kV feeder VT requirements
|  | Type | 3-Phase Inductive | 679; 688 | Appendix IX – 110 kV feeder VT requirements
| HS Earth SW | No. | 1 / Feeder Bay | 50 | 4.02.A.1.1A / 1.1B
|  | Rating | 1600 A | 50 | 4.02.A.1.1A / 1.1B
| Earth SW | No. | 3 / Feeder Bay | 50 | 4.02.A.1.1A / 1.1B
|  | Rating | 1600 A | 50 | 4.02.A.1.1A / 1.1B
| CB | Feeder / Transformer Bay | 1600 A | 50-51 | 4.02.A.1.1A–1.2
|  | Bus Coupler / Bus Section | 2000 A | 52 | 4.02.A.1.3–1.5
|  | Short Circuit | 40 kA / 1 s | 49 | 4.02.A.1
| CT in OHL | CT Before CB Core 1 | 800/1000/1200/1600 : 1 A, Class 0.2FS5 | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT Before CB Core 2 | 800/1000/1200/1600 : 1 A, Class 0.2FS5 | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT Before CB Core 3 | 2000 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT Before CB Core 4 | 2000 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT After CB Core 1 | 800/1000/1200/1600 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT After CB Core 2 | 800/1000/1200/1600 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT After CB Core 3 | 800/1000/1200/1600 : 1 A, Class PX | 679 | Appendix IX – 110 kV OHL feeder protection
|  | CT After CB Core 4 | NA | NA | NA
| CT in Cable Feeder | CT Before CB Core 1 | 800/1000/1200/1600 : 1 A, Class 0.2FS5 | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT Before CB Core 2 | 800/1000/1200/1600 : 1 A, Class 0.2FS5 | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT Before CB Core 3 | 2000 : 1 A, Class PX | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT Before CB Core 4 | 2000 : 1 A, Class PX | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT After CB Core 1 | 1200/1600 : 1 A, Class PX | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT After CB Core 2 | 1200/1600 : 1 A, Class PX | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT After CB Core 3 | 1200/1600 : 1 A, Class PX | 687-688 | Appendix IX – 110 kV U/G cable feeder protection
|  | CT After CB Core 4 | NA | NA | NA
| CT in Transformer Feeder | CT Before CB Core 1 | 300/600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT Before CB Core 2 | 300/600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT Before CB Core 3 | 300/600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT Before CB Core 4 | NA | NA | NA
|  | CT After CB Core 1 | 300/600 : 1 A, Class 0.2FS5 | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT After CB Core 2 | 2000 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT After CB Core 3 | 2000 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | CT After CB Core 4 | NA | NA | NA
| Bus Coupler | No. | 2 | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | Earth SW No. | 2 | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | Earth SW Rating | 2000 A | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CB Rating | 2000 A | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT Before CB Core 1 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT Before CB Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT Before CB Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT Before CB Core 4 | NA | NA | NA
|  | CT After CB Core 1 | 1000/2000 : 1 A, Class 0.2FS5 | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT After CB Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT After CB Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus coupler protection; 4.02.A.1.3
|  | CT After CB Core 4 | NA | NA | NA
| Bus Section | No. | 1 | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Earth SW No. | 2 | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Earth SW Rating | 2000 A | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay Earth SW No. | 2 | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay Earth SW Rating | 2000 A | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CB Rating | 2000 A | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT Before CB Core 1 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT Before CB Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT Before CB Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT Before CB Core 4 | NA | NA | NA
|  | CT After CB Core 1 | 1000/2000 : 1 A, Class 0.2FS5 | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT After CB Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT After CB Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | CT After CB Core 4 | NA | NA | NA
|  | Lower Bus Section Bay CT 1 Core 1 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 1 Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 1 Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 1 Core 4 | NA | NA | NA
|  | Lower Bus Section Bay CT 2 Core 1 | 1000/2000 : 1 A, Class 0.2FS5 | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 2 Core 2 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 2 Core 3 | 2000 : 1 A, Class PX | 52; 694-695 | Appendix IX – 110 kV busbar / bus section protection; 4.02.A.1.4–1.5
|  | Lower Bus Section Bay CT 2 Core 4 | NA | NA | NA
| GIB | Rating | 110 kV Nominal, 145 kV Rated, 3Ph, 60 Hz, 1600 A, 40 kA/1 s, 40°C | 51 | 4.02.A.1.2
|  | GIB VT Ratio | 110/√3 kV : 115/√3 V : 115/√3 V | 51; 704 | 4.02.A.1.2; Appendix IX – transformer protection VT
|  | GIB VT Burden / Class | 100 VA + 100 VA, Class 0.2/3P, Simultaneous 200 VA | 51; 704 | 4.02.A.1.2; Appendix IX – transformer protection VT
|  | Earth SW No. | 1 | 51 | 4.02.A.1.2
|  | Earth SW Rating | 1600 A | 51 | 4.02.A.1.2
|  | SF6 / Air Bushing | 145 kV Class | 51 | 4.02.A.1.2
|  | GIS-to-Transformer Conductor | 1 × 795 kcmil ACSR/AW / Phase | 58 | 4.02.A.5.c
Power Transformer | Rating | Voltage | 110/13.8/6.6 kV | 54 | 4.02.A.2.1
|  | Power | 50/67 MVA | 54 | 4.02.A.2.1
|  | Frequency | 60 Hz | 54 | 4.02.A.2.1
|  | Cooling | ONAN/ONAF | 54 | 4.02.A.2.1
|  | Vector Group | YNyn0 (+d1) | 54 | 4.02.A.2.1
|  | Impedance | 22% @ 50 MVA | 54 | 4.02.A.2.1
|  | OLTC | +12.5% to -20%, Step 1.25% | 54 | 4.02.A.2.1
|  | Ambient Temperature | 55°C | — | —
| No. | Main | 2 | 54 | 4.02.A.2.1
|  | Future | NA | NA | NA
|  | Spare | NA | NA | NA
| SA | Rating | 96 kV, 20 kA, 10 kJ, Class SM | 54 | 4.02.A.2.2; 35-TMSS-01
| CB | Rating | 1600 A (GIS Transformer Feeder CB) | 51 | 4.02.A.1.2
| Earth SW | Rating | 1600 A | 51 | 4.02.A.1.2
| Bushing CT | HV Phase CT Cores 1-3 | 300/600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | HV WTI CT | 530/2 A, Class 3, 30 VA | — | —
|  | HV Neutral CT | 300/600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | MV Phase CT Cores 1-2 | 3600 : 1 A, Class PX | 703-704 | Appendix IX – 50/67 MVA transformer protection
|  | LV WTI CT | 3370/2 A, Class 3, 30 VA | — | —
|  | AVR CT | 2803/5 A, Class 1, 50 VA | — | —
|  | Neutral SBEF CT | 800/1500 : 1 A, Class 10P10, 30/56 VA | 703-704 | Appendix IX – 50/67 MVA transformer protection
NGR | No. | Main | 2 | 54 | 4.02.A.2.3
| Rating | Resistance | 5.3 Ω | 54 | 4.02.A.2.3
|  | Current / Time | 1500 A / 10 s | 54 | 4.02.A.2.3
|  | Built-in Equipment | DS + CT | 54 | 4.02.A.2.3
| Neutral Cable | Rating | 1C × 630 mm² Cu XLPE | 57 | 4.02.A.5.a.iii
SWGR | Rating | System | 13.8 kV Nominal, 17.5 kV Max, 3Ph, 60 Hz | 55; 224-225 | 4.02.A.3; Appendix II / 32-TMSS-01 data schedule
|  | Main Bus | 3600 A | 55; 224-225 | 4.02.A.3; Appendix II / 32-TMSS-01 data schedule
|  | Short Circuit | 25 kA / 3 s | 55; 224-225 | 4.02.A.3; Appendix II / 32-TMSS-01 data schedule
|  | BIL | 95 kV | 224-225 | Appendix II / 32-TMSS-01 data schedule
|  | Power Frequency Withstand | 38 kV | 224-225 | Appendix II / 32-TMSS-01 data schedule
|  | Ambient Temperature | 40°C | 224-225 | Appendix II / 32-TMSS-01 data schedule
| Bus | No. | 2 | — | —
| Transformer Incomer | No. | 2 | 55 | 4.02.A.3.2
|  | CB | 3150 A Natural Cooling / 3600 A Forced Cooling | 55 | 4.02.A.3.2
| Bus Section | No. | 1 | 55 | 4.02.A.3.1
|  | CB | 3600 A | 55 | 4.02.A.3.1
| STATCOM Feeder | No. | 2 | 55 | 4.02.A.3.4
|  | CB | 1250 A | 55 | 4.02.A.3.4
| Aux Transformer Feeder | No. | 2 | 55 | 4.02.A.3.3
|  | CB | 630 A | 55 | 4.02.A.3.3
| Outgoing Feeder | No. | 4 | 55 | 4.02.A.3.5
|  | CB | 630 A | 55 | 4.02.A.3.5
| Future Feeder | No. | 12 | 55 | 4.02.A.3.6
| VT | Ratio | 13.8/√3 kV : 120/√3 V : 120/√3 V | 704; 732 | Appendix IX – transformer / 13.8 kV VT requirements
|  | Burden / Class | 25 VA, Class 0.2 & 3P | 704; 732 | Appendix IX – transformer / 13.8 kV VT requirements
|  | Primary Fuse | 3 A | — | —
| Plain Feeder CT | Protection CT | 1250-800-400 : 1 A, Class 5P20, 30 VA @ 400/1 A | 708 | Appendix IX – 13.8 kV feeder protection
| SIS Busbar | Rating | 13.8 kV, 3600 A, 60 Hz, 25 kA/3 s, 55°C | 58 | 4.02.A.5.d
Aux Transformer | Feeder No. | Main | 2 | 60 | 4.02.A.8.1
| Rating | Voltage | 13.8/0.4 kV | 60 | 4.02.A.8.1
|  | Power | 1000 kVA | 60 | 4.02.A.8.1
|  | Phase / Frequency | 3Ph, 60 Hz | 60 | 4.02.A.8.1
|  | Cooling | ONAN | 60 | 4.02.A.8.1
|  | Vector Group | Dyn11 | 60 | 4.02.A.8.1
|  | Impedance | 5% | 60 | 4.02.A.8.1
| MV Cable | Rating | 15 kV, 1 × 3C × 300 mm² Cu XLPE | 57 | 4.02.A.5.a.ii
STATCOM | No. | Main | 2 | 57 | 4.02.A.4
| Rating | Reactive Power | ±20 MVAr Each | 57 | 4.02.A.4
|  | Voltage | 13.8 kV | 57 | 4.02.A.4
|  | Overload | 20% for 2 s | 2773 | Part II 4.02 – performance requirements
| Feeder CB | Rating | 1250 A | 55 | 4.02.A.3.4
| MV Cable | Rating | 15 kV, 2 × 1C × 630 mm² Cu XLPE / Phase | 57-58 | 4.02.A.5.e.i
| Cable Sealing End | Rating | 13.8 kV, 1250 A, 25 kA/3 s | 59 | 4.02.A.5.e.ii
| IGBT Valve Container | Rating | Vendor Design / Included in ±20 MVAr STATCOM | 2776 | Part II – Converter valve requirements
| Start-up Container | Rating | Vendor Design / Included in ±20 MVAr STATCOM | 2776-2777 | Part II – STATCOM auxiliary/start-up equipment
Other Typical SLD Components | CVT / CCVT | Rating | NA | NA | NA
| Line Trap / Wave Trap | Rating | NA | NA | NA
| Shunt Capacitor Bank | Rating | NA | NA | NA
| Shunt Reactor | Rating | NA | NA | NA
| Bus Reactor | Rating | NA | NA | NA
| Series Reactor | Rating | NA | NA | NA
| Grounding Transformer | Rating | NA | NA | NA
| Petersen Coil | Rating | NA | NA | NA
| AIS 110 kV CB / DS | Rating | NA | NA | NA
| RMU | Rating | NA | NA | NA
| HV Cable Link Box / SVL | Rating | NA | NA | NA
| Diesel Generator | Rating | NA | NA | NA
| UPS | Rating | NA | NA | NA
| Station Battery / Charger | Rating | NA | NA | NA
| Main ACDB | Rating | NA | NA | NA
| Main DCDB | Rating | NA | NA | NA